## buses
| label | comment | active | excess | shortage | excess costs | shortage costs | excess constraint costs | shortage constraint costs | district heating conn. | lat | lon | sector
1 | ID_electricity_bus | The "ID_electricity_bus" is used to represent the electricity bus of the "ID" building. It is provided with a shortage (shortage = 1), which represents the purchase of electricity from the network. Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 0 | 1 | 0 | 0.3 | 0 | 474 | 0 | 0 | 0 | electricity
2 | ID_heat_bus | The "ID_heat_bus" is used to represent the heat bus of the "ID" building. This bus has neither a shortage nor an excess, since heat in the example can neither be supplied to the environment (excess) nor purchased (shortage). A heating network is an investment alternative for the heat bus (district heating conn. = 1). | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0401 | 7.02 | heat
3 | ID_gas_bus | The "ID_gas_bus" is used to represent the gas bus of the "ID" building. It is provided with a shortage (shortage = 1), which represents the purchase of gas from the network. Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 0 | 1 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | None
4 | ID_cooling_bus | The "ID_cooling_bus" is used to represent the cooling bus of the "ID" building. This bus has neither a shortage nor an excess. A heating network is not an investment alternative for the cooling bus (district heating conn. = 0). | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | cooling
5 | ID_pv_bus | The PV systems of the building "ID" are connected to the "ID_pv_bus". This bus is equipped with an excess (excess = 1), which makes it possible to sell surplus electricity to the grid (outside the balance limit). Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 1 | 0 | -0.068 | 0 | -56 | 0 | 0 | 0 | 0 | electricity
6 | ID_hp_electricity_bus | The "ID_hp_electricity_bus" is necessary since there is often a separate electricity tariff for heat pumps. Consequently, the heat pumps are connected to this bus, which has a more favorable shortage than the "ID_electricity_bus". Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 0 | 1 | 0 | 0.22 | 0 | 474 | 0 | 0 | 0 | electricity
7 | district_electricity_bus | The bus "district_electricity_bus" would allow to exchange electricity between two buildings by connecting them with a link to this bus. Since only one building is considered in the example, this bus is deactivated (active = 0). Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | central_electricity
8 | district_chp_electricity_bus | The bus "district_chp_electricity_bus" allows the sale of the surplus electricity produced by CHP units to the grid (outside the balance limits). Here, the emissions accounted for the electricity amount are compensated (excess constraint costs = -375). Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 1 | 0 | -0.0682 | 0 | -375 | 0 | 0 | 0 | 0 | central_electricity
9 | district_gas_bus | The bus "district_gas_bus" represents the gas purchase for the central gas-powered plants, for example, CHPs. For this purpose, the bus is provided with a shortage (shortage = 1). Obviously, this bus is not connected to the heating network (district heating conn. = 0). | 1 | 0 | 1 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | None
10 | district_heat_bus | The "district_heat_bus" represents the output bus of the central heat generators and the input to the heating network (district heating conn. = dh-system). Since in the example no purchase or sale of heat across the balance boundaries is possible, there is neither excess nor shortage. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.0401 | 7.0201 | central_heat

## sources
| label | comment | active | fixed | sector | technology | output | input | existing capacity | min. investment capacity | max. investment capacity | non-convex investment | fix investment costs | fix investment constraint costs | variable costs | periodical costs | variable constraint costs | periodical constraint costs | Turbine Model | Hub Height | Modul Model | Inverter Model | Albedo | Altitude | Azimuth | Surface Tilt | Latitude | Longitude | ETA 0 | A1 | A2 | C1 | C2 | Temperature Inlet | Temperature Difference | Conversion Factor | Peripheral Losses | Electric Consumption | Cleanliness
1 | ID_photovoltaic_electricity_source | The "ID_photovoltaic_electricity_source" the investment option of a photovoltaic system with a maximum capacity of 20 kW. The load profile is automatically calculated based on the given parameters. Beside the green ones, the blue columns are relevant for this component. Several parameters such as the location, azimuth and tilt of the modules are individually defined. Technical parameters of the module and the inverter are automatically obtained from a coupled database. | 1 | 1 | electricity | photovoltaic | ID_pv_bus | None | 0 | 18 | 18 | 0 | 0 | 0 | 0 | 90 | 56 | 0 | 0 | 0 | Panasonic_VBHN235SA06B__2013_ | ABB__MICRO_0_25_I_OUTD_US_240__240V_ | 0.18 | 60 | 180 | 35 | 52.13 | 7.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | ID_solar_thermal_source | The "ID_solar_thermal_source" represents the investment option of a solar thermal system with a maximum capacity of 20 kW. The load profile is automatically calculated based on the given parameters. Beside the green ones, the blue columns are relevant for this component. Several parameters such as the location and otientation of the modules are defined, as well as technical parameters of the system. | 1 | 1 | heat | solar_thermal_flat_plate | ID_heat_bus | ID_electricity_bus | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 52.13 | 7.36 | 0.719 | 1.063 | 0.005 | 0 | 0 | 40 | 15 | 1.8994 | 0.05 | 0.06 | 0
3 | wind_turbine | The "wind_turbine" source represents the investment option of a wind turbine with a maximum capacity of 30 kW. This component is deactivated and will not be considered during the modeling process. The load profile is automatically calculated based on the given parameters. Beside the green ones, the red columns are relevant for this component. Several parameters such as the hub hight are defined. Technical parameters of the turbine model are automatically obtained from a coupled data base. | 0 | 1 | electricity | windpower | ID_pv_bus | None | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | E-126/4200 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## transformers
| label | comment | active | sector | technology | transformer type | mode | input | output | output2 | efficiency | efficiency2 | existing capacity | min. investment capacity | max. investment capacity | non-convex investment | fix investment costs | fix investment constraint costs | variable input costs | variable output costs | variable output costs 2 | periodical costs | variable input constraint costs | variable output constraint costs | variable output constraint costs 2 | periodical constraint costs | heat source | temperature high | temperature low | quality grade | area | length of the geoth. probe | heat extraction | min. borehole area | temp. threshold icing | factor icing | name | high temperature | chilling temperature | electrical input conversion factor | recooling temperature difference | heat capacity of source | min. share of flue gas loss | max. share of flue gas loss | min. electric power | max. electric power | min. electric efficiency | max. electric efficiency | minimal thermal output power | elec. power loss index | back pressure
1 | ID_gasheating_transformer | This transformer represents the investment option for a natural gas heating system with a maximum capacity of 20 kW. Only the green columns are relevant for this component. | 1 | heat | nautral_gasheating | GenericTransformer | 0 | ID_gas_bus | ID_heat_bus | None | 0.85 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | ID_GCHP_transformer | This transformer represents the investment option for a ground-coupled heat pump with a maximum capacity of 20 kW. Beside the green ones, the red columns are relevant for this component. Several parameters are defined, which are relevant for the calculation of an individual load profile, for which also the data stored in the "weather data" sheet are considered. | 1 | heat | GCHP | CompressionHeatTransformer | heat_pump | ID_hp_electricity_bus | ID_heat_bus | None | 1 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 115.57 | 0 | 0 | 0 | 0 | Ground | 60 | 0 | 0.6 | 1000 | 100 | 0.05 | 100 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | ID_ASCH_transformer | This transformer represents the investment option for an air source chiller with a maximum capacity of 20 kW. Beside the green ones, the red columns are relevant for this component. Several parameters are defined, which are relevant for the calculation of an individual load profile, for which also the data stored in the "weather data" sheet are considered. | 1 | cooling | ASCH | CompressionHeatTransformer | chiller | ID_hp_electricity_bus | ID_cooling_bus | None | 1 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | Air | 0 | -10 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | ID_AbsCH_transformer | This transformer represents the investment option for an absorption chiller with a maximum capacity of 20 kW. Beside the green ones, the blue columns are relevant for this component. Several parameters are defined, which are relevant for the calculation of an individual load profile, for which also the data stored in the "weather data" sheet are considered. | 1 | cooling | AbsCH | AbsorptionHeatTransformer | chiller | ID_hp_electricity_bus | ID_cooling_bus | None | 1 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Kuehn | 85 | 10 | 0.05 | 6 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | ID_ASHP_transformer | This transformer represents the investment option for an air source heat pump with a maximum capacity of 20 kW. Beside the green ones, the red columns are relevant for this component. Several parameters are defined, which are relevant for the calculation of an individual load profile, for which also the data stored in the "weather data" sheet are considered. | 1 | heat | ASHP | CompressionHeatTransformer | heat_pump | ID_hp_electricity_bus | ID_heat_bus | None | 1 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 112.78 | 0 | 0 | 0 | 0 | Air | 60 | 0 | 0.4 | 0 | 0 | 0 | 0 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | ID_chp_transformer | This transformer represents the investment option for a centralized combined heat and power plant with a maximum capacity of 20 kW. As it has two energy outputs, there are two efficiencies given, one for each energy output. Only the green columns are relevant for this component. | 1 | heat | natural_gas_CHP | GenericTransformer | 0 | district_gas_bus | district_chp_electricity_bus | district_heat_bus | 0.35 | 0.55 | 0 | 6219 | 6219 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 130 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## storages
| label | comment | active | sector | storage type | bus | input/capacity ratio | output/capacity ratio | efficiency inflow | efficiency outflow | initial capacity | capacity min | capacity max | existing capacity | min. investment capacity | max. investment capacity | non-convex investment | fix investment costs | fix investment constraint costs | variable input costs | variable output costs | periodical costs | variable input constraint costs | variable output constraint costs | periodical constraint costs | capacity loss | diameter | temperature high | temperature low | U value
1 | ID_battery_storage | This storage represents the investment option of a decentralized (it is connected to the "ID_electricity_bus") battery storage with a maximum capacity of 100 kWh. Several parameters are defined which influence the charging and discharging behavior as well as losses of the storage. The values of min. and max. capacity are realtive values to the nominal capacity. The inital capacity must be at least as big as the min capacity. | 1 | electricity | Generic | ID_electricity_bus | 0.17 | 0.17 | 1 | 0.98 | 0.1 | 0.1 | 1 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0
2 | ID_thermal_storage | This storage represents the investment option of a decentralized (it is connected to the "ID_heat_bus") thermal storage with a maximum capacity of 100 kWh. Several parameters are defined which influence the charging and discharging behavior as well as losses of the storage. The values of min. and max. capacity are realtive values to the nominal capacity. The inital capacity must be at least as big as the min capacity. | 1 | heat | Generic | ID_heat_bus | 0.17 | 0.17 | 1 | 0.98 | 0.1 | 0.1 | 0.9 | 0 | 26 | 26 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0
3 | ID_stratified_thermal_storage | This storage represents the investment option of a stratified storage with a maximum capacity of 100 kWh. This component is deactivated and will not be considered during the modeling process. Several parameters are defined which influence the charging and discharging behavior as well as losses of the storage. The values of min. and max. capacity are realtive values to the nominal capacity. The inital capacity must be at least as big as the min capacity. | 0 | heat | Stratified | ID_heat_bus | 0.2 | 0.2 | 1 | 0.98 | 0.05 | 0.05 | 0.95 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 100 | 0 | 0.8 | 60 | 40 | 0.04
4 | district_battery_storage | This storage represents the investment option of a centralized (it is connected to the "district_electricity_bus") battery storage with a maximum capacity of 100 kWh. This component is deactivated and will not be considered during the modeling process. Several parameters are defined which influence the charging and discharging behavior as well as losses of the storage. The values of min. and max. capacity are realtive values to the nominal capacity. The inital capacity must be at least as big as the min capacity. | 0 | electricity | Generic | district_electricity_bus | 0.17 | 0.17 | 1 | 0.98 | 0.1 | 0.1 | 1 | 0 | 499 | 499 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0

## links
| label | comment | active | (un)directed | bus1 | bus2 | efficiency | existing capacity | min. investment capacity | max. investment capacity | non-convex investment | fix investment costs | fix investment constraint costs | variable output costs | periodical costs | variable output constraint costs | periodical constraint costs
1 | ID_pv_to_ID_electricity_link | This link represents the investment option of a directed, loss-free (efficiency=1) electricity link between "ID_pv_bus" and "ID_electricity_bus" with a maximum capacity of 20 kW. It is used to transfer electricity from the buildings pv-system to the building electricity system. | 1 | directed | ID_pv_bus | ID_electricity_bus | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | ID_electricity_to_ID_hp_electricity_bus | This link represents the investment option of a directed, loss-free (efficiency=1) electricity link between "ID_electricity_bus" and "ID_hp_electricity_bus" with a maximum capacity of 20 kW. It is used to transfer electricity from the buildings main electricity system to its heat pumps. | 1 | directed | ID_electricity_bus | ID_hp_electricity_bus | 1 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | districtheat_directed_link | This link represents the investment option of a directed, loss-making (efficiency=0.85) district heating link between "district_heat_bus" and "ID_hp_heat_bus" with a maximum capacity of 20 kW. It is used to transfer heat from the district heating system to the buildings heat system. This component is deactivated and will not be considered during the modeling process. | 0 | directed | district_heat_bus | ID_heat_bus | 0.85 | 0 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | districtheat_undirected_link | This link represents the investment option of a undirected, loss-making (efficiency=0.85) district heating link between "district_heat_bus" and "ID_hp_heat_bus" with a maximum capacity of 20 kW. It is used to transfer heat from the district heating system to the buildings heat system or reverse. This component is deactivated and will not be considered during the modeling process. | 0 | undirected | district_heat_bus | ID_heat_bus | 0.85 | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | district_electricity_link | This link represents the investment option of a directed, loss-free (efficiency=1) electricity link between "district_electricity_bus" and "ID_electricity_bus" with a maximum capacity of 20 kW. It is used to transfer electricity from the district electricity system to the ID-building electricity system. For the transport costs of 0.1438 €/kWh apply. This component is deactivated and will not be considered during the modeling process. | 0 | directed | district_electricity_bus | ID_electricity_bus | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1438 | 0 | 0 | 0
6 | district_chp_to_district_electricity_bus | This link represents the investment option of a directed, loss-free (efficiency=1) electricity link between "district_chp_electricity_bus" and "district_electricity_bus" with a maximum capacity of 20 kW. It is used to transfer electricity from the centralized chp to the districts main electricity system. For the transport costs of 0.1438 €/kWh apply. This component is deactivated and will not be considered during the modeling process. | 0 | directed | district_chp_electricity_bus | district_electricity_bus | 1 | 0 | 14 | 14 | 0 | 0 | 0 | 0.1438 | 0 | 0 | 0
7 | ID_pv_to_district_electricity_link | This link represents the investment option of a directed, loss-free (efficiency=1) electricity link between "ID_pv_bus" and "district_electricity_bus" with a maximum capacity of 20 kW. It is used to transfer electricity from ID-buildings pv system to the districts electricity bus. For the transport costs of 0.1438 €/kWh apply. This component is deactivated and will not be considered during the modeling process. | 0 | directed | ID_pv_bus | district_electricity_bus | 1 | 0 | 8 | 8 | 0 | 0 | 0 | 0.1438 | 0 | 0 | 0

## insulation
| label | comment | active | sink | temperature indoor | heat limit temperature | U-value old | U-value new | area | periodical costs | periodical constraint costs | existing | existing with costs
1 | ID_heat_sink_window | This insulation measure (ID_heat_sink_window) represents insulation of the windows from a U-value of 2.8(old) to 0.825 (new). This is represented in the energy system as a source that, when invested, covers part of the heat demand (reduces it). The amount of energy provided by an insulation measure then no longer needs to be provided by heat supply technologies. | 1 | ID_heat_sink | 20 | 15 | 2.8 | 0.825 | 93.0177 | 2400 | 21.9 | 0 | 0

## district heating
| label | comment | lat. 1st intersection | lat. 2nd intersection | lon. 1st intersection | lon. 2nd intersection | active
1 | ID_street1 | This entry (ID_street1) represents a street section that is eligible for the installation of a heat network distribution line. This is bounded by the 1st intersection (represented by its longitude and latitude) and the 2nd intersection (represented by its longitude and latitude) as a route. Potential consumers and producers (buses sheet) are connected to this route via an automatic perpendicular point search. | 50.03 | 50.05 | 7.015 | 7.025 | 0